Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 26					CABLE TRAYS FOR ELECTRICAL SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Ladder cable trays.

Single-rail cable trays.

Trough (solid) cable trays.

Fiberglass cable trays.

Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 270536 "Cable Trays for Communications Systems" for cable trays and accessories serving communications systems.

ACTION SUBMITTALS

Product Data: For each type of product.

Include data indicating dimensions and finishes for each type of cable tray indicated.

Shop Drawings: For each type of cable tray.

Show fabrication and installation details of cable trays, including plans, elevations, and sections of components and attachments to other construction elements. Designate components and accessories, including clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, and fittings.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

Delegated-Design Submittal: For seismic restraints.

Seismic-Restraint Details: Signed and sealed by a qualified professional engineer, licensed in the state where Project is located and who is responsible for the preparation.

Design Calculations: Calculate requirements for selecting seismic restraints.

Detail fabrication, including anchorages and attachments to structure and to supported cable trays.

INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

Coordination Drawings: Floor plans and sections, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:.

Include scaled cable tray layout and relationships between components and adjacent structural, electrical, and mechanical elements.

Vertical and horizontal offsets and transitions.

Clearances for access above and to side of cable trays.

Vertical elevation of cable trays above the floor or below bottom of ceiling structure.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

Seismic Qualification Certificates: For cable trays, accessories, and components, from manufacturer.

Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Field quality-control reports.

PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design cable tray supports and seismic bracing.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

Seismic Performance: Cable trays and supports shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification.

The term "withstand" means "cable trays will remain in place without separation of any parts when subjected to the seismic forces specified."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table for requirements to be inserted in subparagraph below.

<Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

Thermal Movements: Allow for thermal movements from ambient and surface temperature changes in cable tray installed outdoors.

Differential values in "Temperature Change" Subparagraph below (for aluminum in particular) are suitable for most of the U.S.

Temperature Change: [120 deg F (67 deg C), ambient; 180 deg F (100 deg C), material surfaces] <Insert temperature change>.

GENERAL REQUIREMENTS FOR CABLE TRAYS

If cable trays are identified for use via listing, then follow listing requirements. This may require that all interconnected cable trays be from single manufacturer. Some tray types may not be capable of being interconnected.

Cable Trays and Accessories: Identified as defined in NFPA 70 and marked for intended location, application, and grounding.

Source Limitations: Obtain cable trays and components from single manufacturer.

If using multiple types, sizes, or ratings of cable trays on a project, consider adding a table to Drawings.

Sizes and Configurations: See the Cable Tray Schedule on Drawings for specific requirements for types, materials, sizes, and configurations.

Structural Performance: See articles on individual cable tray types for specific values for the following parameters:

See "Load/Span Classification System" Article in the Evaluations.

Uniform Load Distribution: Capable of supporting a uniformly distributed load on the indicated support span when supported as a simple span and tested according to NEMA VE 1.

Concentrated Load: A load applied at midpoint of span and centerline of tray.

Load and Safety Factors: Applicable to both side rails and rung capacities.

LADDER CABLE TRAYS

Basis-of-Design Product: Subject to compliance with requirements of a comparable product by one of the following:

Allied Tube & Conduit.

Basor Electric – Cable Tray

Chalfant Manufacturing Company.

Cooper B-Line, Inc.; a division of Cooper Industries.

MonoSystems, Inc.

Niedax Inc.

Description:

Configuration: Two I-beam side rails with transverse rungs welded to side rails.

Rung Spacing: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] o.c.

Radius-Fitting Rung Spacing: 9 inches (225 mm) at center of tray's width.

Minimum Cable-Bearing Surface for Rungs: 7/8-inch (22-mm) width with radius edges.

No portion of the rungs shall protrude below the bottom plane of side rails.

Structural Performance of Each Rung: Capable of supporting a maximum cable load, with a safety factor of 1.5, plus a200-lb (90-kg) concentrated load, when tested according to NEMA VE 1.

Minimum Usable Load Depth: [3 inches (75 mm)] [4 inches (100 mm)] [5 inches (125 mm)] [6 inches (150 mm)].

Straight Section Lengths: [10 feet (3 m)] [12 feet (3.6 m)] [20 feet (6 m)] [24 feet (7.4 m)] [30 feet (9 m)] except where shorter lengths are required to facilitate tray assembly.

Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] [30 inches (750 mm)] [36 inches (900 mm)] unless otherwise indicated on Drawings.

Fitting Minimum Radius: [12 inches (300 mm)] [24 inches (600 mm)] [36 inches (900 mm)] [48 inches (1200 mm)].

The maximum uniform load and the support span are indicated by the cable tray class.

Class Designation: Comply with NEMA VE 1, [Class 12B] [Class 12C] [Class 20B] [Class 20C] <Insert designation>.

Splicing Assemblies: Bolted type using serrated flange locknuts.

Hardware and Fasteners: [ASTM F 593 and ASTM F 594 stainless steel, Type 316] [Steel, zinc plated according to ASTM B 633].

Splice Plate Capacity: Splices located at quarter support span shall not diminish rated loading capacity of cable tray.

SINGLE-RAIL CABLE TRAYS

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

Allied Tube & Conduit.

Basor Electric – Cable Tray

Cooper B-Line, Inc.; a division of Cooper Industries.

MonoSystems, Inc.

MP Husky USA Cable Tray & Cable Bus.

Description:

Configuration: Center rail with extruded-aluminum rungs arranged symmetrically about the center rail.

Construction: Aluminum rungs mechanically connected to aluminum center rail in at least two places, with ends finished to protect installers and cables.

Rung Spacing: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] o.c.

Radius-Fitting Rung Spacing: 9 inches (225 mm) at center of tray's width.

Straight Section Lengths: [10 feet (3 m)] [12 feet (3.6 m)] except where shorter lengths are required to facilitate tray assembly.

Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] unless otherwise indicated on Drawings.

Support Point: Splice fittings shall be hanger support point.

Support Spacing: Support each section at midpoint. Support wall-mounted sections a maximum of one-sixth of the section length from each end.

Loading Depth: [3 inches (75 mm)] [4 inches (100 mm)] [6 inches (150 mm)].

Maximum Loads: [25 lb/ft. (37 kg/m)] [50 lb/ft. (74 kg/m)].

Maintaining cable tray rungs within six degrees of horizontal is for aesthetic reasons. The tray looks uneven when tilted more than this. Support variations are available to allow varying levels of unbalanced loads while not exceeding the maximum tilt.

Unbalanced Loads: Maintain cable tray rungs within six degrees of horizontal under all loading conditions.

Splicing Assemblies: Bolted type using serrated flange locknuts.

Splicing Assembly Capacity: Splices located within support span shall not diminish rated loading capacity of cable tray.

Hardware and Fasteners: [ASTM F 593 and ASTM F 594 stainless steel, Type 316] [Steel, zinc plated according to ASTM B 633].

Splices and Connectors: Protect cables from edges of center rail and do not intrude into cable fill area.

TROUGH (SOLID) CABLE TRAYS

Basis-of-Design Product: Subject to compliance with requirements a comparable product by one of the following:

Allied Tube & Conduit.

BASOR Tray

Cablofil; Legrand.

Chalfant Manufacturing Company.

Cooper B-Line, Inc.; a division of Cooper Industries.

MonoSystems, Inc.

MP Husky USA Cable Tray & Cable Bus.

Niedax Inc.

Description:

Configuration: Two longitudinal members (side rails) with a solid sheet over rungs exposed on the interior of the trough, or corrugated sheet with both edges welded to the side rails.

Rung Spacing: Rungs or corrugations shall be spaced a maximum of 12 inches (300 mm) o.c. and have a minimum flat bearing surface of 1.8 inches (46 mm).

Radius-Fitting Rung Spacing: 9 inches (225 mm) at center of tray's width.

Structural Performance: Capable of supporting a maximum cable load, with a safety factor of 1.5, plus a 200-lb (90-kg) concentrated load, when tested according to NEMA VE 1.

Minimum Usable Load Depth: [3 inches (75 mm)] [4 inches (100 mm)] [5 inches (125 mm)] [6 inches (150 mm)].

Straight Section Lengths: [10 feet (3 m)] [12 feet (3.6 m)] [20 feet (6 m)] [24 feet (7.4 m)] [30 feet (9 m)] except where shorter lengths are required to facilitate tray assembly.

Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] [30 inches (750 mm)] [36 inches (900 mm)] unless otherwise indicated on Drawings.

Fitting Minimum Radius: [12 inches (300 mm)] [24 inches (600 mm)] [36 inches (900 mm)] [48 inches (1200 mm)].

The maximum uniform load and the support span are indicated by the cable tray class.

Class Designation: Comply with NEMA VE 1, [Class 12B] [Class 12C] [Class 20B] [Class 20C] <Insert designation>.

Splicing Assemblies: Bolted type using serrated flange locknuts.

Splicing Assembly Capacity: Splices located at quarter support span shall not diminish rated loading capacity of cable tray.

Hardware and Fasteners: [ASTM F 593 and ASTM F 594 stainless steel, Type 316] [Steel, zinc plated according to ASTM B 633].

FIBERGLASS CABLE TRAYS

Basis-of-Design Product: Subject to compliance with requirements a comparable product by one of the following:

Allied Tube & Conduit.

Basor Electric – Cable Tray

Cooper B-Line, Inc.; a division of Cooper Industries.

Enduro Composites Inc.

MonoSystems, Inc.

MP Husky USA Cable Tray & Cable Bus.

PW Legrand.

Description:

Configuration: Two longitudinal members with rounded edges and smooth surfaces, complying with NEMA FG 1.

Materials: Straight section structural elements; side rails, rungs and splice plates shall be pultruded from glass-fiber-reinforced [polyester] [vinyl ester] resin, complying with NEMA FG 1 and UL 568.

Fasteners: Fiberglass-encapsulated, ASTM F 593 and ASTM F 594 stainless steel, Type 316. Design fasteners so that no metal is visible when fully assembled and tightened. Fastener encapsulation shall not be damaged when torqued to manufacturer's recommended value.

Minimum Usable Load Depth: [2 inches (50 mm)] [3 inches (75 mm)] [5 inches (125 mm)] according to NEMA FG 1.

Straight Section Lengths: [10 feet (3 m)] [20 feet (6 m)].

Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] [30 inches (750 mm)] [36 inches (900 mm)] unless otherwise indicated on Drawings.

The maximum uniform load and the support span are indicated by the cable tray class.

Class Designation: Comply with NEMA VE 1, [Class 12B] [Class 12C] [Class 20B] [Class 20C] <Insert designation>.

See "Load/Span Classification System" Article in the Evaluations for discussion of temperature effects.

Temperature Rating: Reduce the load rating of tray exposed to temperatures above 75 deg F (24 deg C) according to Table 4-3, "Working Loads," in NEMA FG 1.

Fitting Minimum Radius: [12 inches (300 mm)] [24 inches (600 mm)] [36 inches (900 mm)].

Splicing Assemblies: Minimum four nuts and bolts per plate. Splice plates shall be furnished with straight sections and fittings.

Splicing Assembly Capacity: Splices located at quarter support span shall not diminish rated loading capacity of cable tray.

MATERIALS AND FINISHES

Retain one or more of "Steel," "Aluminum," and "Stainless Steel" paragraphs below. If using more than one type of cable tray material for Project, consider using a schedule to detail the specific requirements in each area. See "Cable Tray Materials" Article in the Evaluations.

Steel:

ASTM A 1011/A 1011M is for 14 gage and thicker; ASTM A 1008/A 1008M is for 16 gage and thinner. Both have structural-steel (SS) and high-strength, low-alloy-steel (HSLAS) designations.

Straight Section and Fitting Side Rails and Rungs: Steel complies with the minimum mechanical properties of [ASTM A 1011/A 1011M, SS, Grade 33] [ASTM A 1008/A 1008M, Grade 33, Type 2].

Steel Tray Splice Plates: ASTM A 1011/A 1011M, HSLAS, Grade 33, Class 1.

Fasteners: Steel complies with the minimum mechanical properties of ASTM A 510/A 510M, Grade 1008.

Retain one of six "Finish" subparagraphs below or insert a different finish.

Finish: Mill galvanized before fabrication.

Standard: Comply with ASTM A 653/A 653M, G90 (Z275).

Retain one option in "Hardware" Subparagraph below.

Hardware: [Galvanized, ASTM B 633] [Chromium-zinc plated, ASTM F 1136].

Finish: Electrogalvanized before fabrication.

Standard: Comply with ASTM B 633.

Hardware: Galvanized, ASTM B 633.

Finish: Hot-dip galvanized after fabrication.

Standard: Comply with ASTM A123/A123 M, Class B2.

Retain one option in "Hardware" Subparagraph below.

Hardware: [Chromium-zinc plated, ASTM F 1136] [Stainless steel, Type 316].

Finish: [Epoxy-resin] [Powder-coat enamel] paint.

Powder-Coat Enamel: Cable tray manufacturer's recommended primer and corrosion-inhibiting treatment, with factory-applied powder-coat paint.

Epoxy-Resin Prime Coat: Cold-curing epoxy primer, MPI# 101.

Epoxy-Resin Topcoat: Epoxy, cold-cured, gloss, MPI# 77.

Retain one option in "Hardware" Subparagraph below.

Hardware: [Chromium-zinc plated. ASTM F 1136] [Stainless steel, Type 316, ASTM F 593 and ASTM F 594].

Finish: Factory-standard primer, ready for field painting, with chromium-zinc-plated hardware according to ASTM F 1136.

Finish: Black oxide finish for support accessories and miscellaneous hardware according to ASTM D 769.

<Insert finish>.

Aluminum:

Materials: Alloy 6063-T6 according to ANSI H35.1/H 35.1M for extruded components, and [Alloy 5052-H32] [or] [Alloy 6061-T6] according to ANSI H35.1/H 35.1M for fabricated parts.

Hardware: [Chromium-zinc-plated steel, ASTM F 1136] [Stainless steel, Type 316, ASTM F 593 and ASTM F 594].

Hardware for Aluminum Cable Tray Used Outdoors: Stainless steel, Type 316, ASTM F 593 and ASTM F 594.

Stainless Steel:

Materials: Low-carbon, passivated, stainless steel, Type 316L, ASTM F 593 and ASTM F 594.

Hardware for Stainless-Steel Cable Tray Used Outdoors: Stainless steel, Type 316, ASTM F 593 and ASTM F 594.

CABLE TRAY ACCESSORIES

Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray.

If more than one cable tray cover type is required, delete "Covers" Paragraph below and indicate type on Drawings or in a schedule. Retain paragraph if cable tray covers are required. See "Cable Tray Covers" Article in the Evaluations.

Covers: [Solid] [Louvered] [Ventilated-hat] [2-in-3 pitch] type made of same materials and with same finishes as cable tray.

Indicate required locations for barrier strips on Drawings.

Barrier Strips: Same materials and finishes as for cable tray.

Cable tray supports and connectors, including bonding jumpers, as recommended by cable tray manufacturer.

WARNING SIGNS

Insert different lettering size in "Lettering" Paragraph below to suit 25-foot (7.6-m) viewing distance.

Lettering: [1-1/2-inch- (40-mm-)] <Insert dimension> high, black letters on yellow background with legend "Warning! Not To Be Used as Walkway, Ladder, or Support for Ladders or Personnel."

Comply with requirements for fasteners in Section 260553 "Identification for Electrical Systems."

SOURCE QUALITY CONTROL

Testing: Test and inspect cable trays according to [NEMA FG 1] [NEMA VE 1].

EXECUTION

CABLE TRAY INSTALLATION

NEMA FG 1 applies to fiberglass cable trays only. NEMA VE 2 applies to all metallic cable trays.

Install cable trays according to [NEMA FG 1] [NEMA VE 2].

Install cable trays as a complete system, including fasteners, hold-down clips, support systems, barrier strips, adjustable horizontal and vertical splice plates, elbows, reducers, tees, crosses, cable dropouts, adapters, covers, and bonding.

Install cable trays so that the tray is accessible for cable installation and all splices are accessible for inspection and adjustment.

Remove burrs and sharp edges from cable trays.

Join aluminum cable tray with splice plates; use four square-neck carriage bolts and locknuts.

Fasten cable tray supports to building structure [and install seismic restraints].

Retain first paragraph below if deleting "Delegated Design" Paragraph in "Performance Requirements" Article. Delete below if retaining "Delegated Design" Paragraph.

Design fasteners and supports to carry cable tray, the cables, and a concentrated load of 200 lb (90 kg). Comply with requirements in Section 260529 "Hangers and Supports for Electrical Systems."[Comply with seismic-restraint details according to Section 260548.16 "Seismic Controls for Electrical Systems."]

Place supports so that spans do not exceed maximum spans on schedules and provide clearances shown on Drawings. Install intermediate supports when cable weight exceeds the load-carrying capacity of the tray rungs.

Construct supports from channel members, threaded rods, and other appurtenances furnished by cable tray manufacturer. Arrange supports in trapeze or wall-bracket form as required by application.

Support bus assembly to prevent twisting from eccentric loading.

Install center-hung supports for single-rail trays designed for 60 versus 40 percent eccentric loading condition, with a safety factor of 3.

Locate and install supports according to [NEMA FG 1] [NEMA VE 2]. Do not install more than one cable tray splice between supports.

Retain first paragraph below if cable trays connect to equipment.

Make connections to equipment with flanged fittings fastened to cable trays and to equipment. Support cable trays independent of fittings. Do not carry weight of cable trays on equipment enclosure.

Retain first paragraph below if expansion fittings are required.

Install expansion connectors where cable trays cross building expansion joints and in cable tray runs that exceed dimensions recommended in [NEMA FG 1] [NEMA VE 2]. Space connectors and set gaps according to applicable standard.

Make changes in direction and elevation using manufacturer's recommended fittings.

Make cable tray connections using manufacturer's recommended fittings.

Seal penetrations through fire and smoke barriers. Comply with requirements in Section 078413 "Penetration Firestopping."

If cable trays are sized for future cables, specify provisions for penetrations with sleeves through fire-rated partitions or use "repairable" firestop-sealing material. Include this Section's specific firestopping requirements in a schedule developed in Section 078413 "Penetration Firestopping."

Install capped metal sleeves for future cables through firestop-sealed cable tray penetrations of fire and smoke barriers.

Install cable trays with enough workspace to permit access for installing cables.

Retain first paragraph below if systems are mixed in a single cable tray.

Install barriers to separate cables of different systems, such as power, communications, and data processing; or of different insulation levels, such as 600, 5000, and 15 000 V.

See "Cable Tray Covers" Article in the Evaluations.

Install permanent covers, if used, after installing cable. Install cover clamps according to NEMA VE 2.

Clamp covers on cable trays installed outdoors with heavy-duty clamps.

Install warning signs in visible locations on or near cable trays after cable tray installation.

CABLE TRAY GROUNDING

Ground cable trays according to NFPA 70 unless additional grounding is specified. Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems."

Cable trays with electrical power conductors shall be bonded together with splice plates listed for grounding purposes or with listed bonding jumpers.

Verify that cable tray system is specified for grounding and bonding the largest power conductor in the tray. If system is not specified, retain first paragraph below and revise to suit Project.

Cable trays with single-conductor power conductors shall be bonded together with a grounding conductor run in the tray along with the power conductors and bonded to the tray at 72-inch (1800-mm) intervals. The grounding conductor shall be sized according to NFPA 70, Article 250.122, "Size of Equipment Grounding Conductors," and Article 392, "Cable Trays."

When using epoxy- or powder-coat painted cable trays as a grounding conductor, completely remove coating at all splice contact points or ground connector attachment. After completing splice-to-grounding-bolt attachment, repair the coated surfaces with coating materials recommended by cable tray manufacturer.

Bond cable trays to power source for cables contained within with bonding conductors sized according to NFPA 70, Article 250.122, "Size of Equipment Grounding Conductors."

CABLE INSTALLATION

Install cables only when each cable tray run has been completed and inspected.

Fastening cables on horizontal runs is beyond the requirements of NFPA 70 in most cases. See Evaluations.

Fasten cables on horizontal runs with cable clamps or cable ties according to NEMA VE 2. Tighten clamps only enough to secure the cable, without indenting the cable jacket. Install cable ties with a tool that includes an automatic pressure-limiting device.

Fasten cables on vertical runs to cable trays every 18 inches (450 mm).

Length of unsupported cable is dependent on the cable diameter. See "Cable Installations" Article in Evaluations.

Fasten and support cables that pass from one cable tray to another or drop from cable trays to equipment enclosures. Fasten cables to the cable tray at the point of exit and support cables independent of the enclosure. The cable length between cable trays or between cable tray and enclosure shall be no more than 72 inches (1800 mm).

Tie MI cables down every 36 inches (900 mm) where required to provide a 2-hour fire rating and every 72 inches (1800 mm) elsewhere.

In existing construction, remove inactive or dead cables from cable trays.

CONNECTIONS

Remove paint from all connection points before making connections. Repair paint after the connections are completed.

Connect raceways to cable trays according to requirements in NEMA VE 2 and NEMA FG 1.

FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

After installing cable trays and after electrical circuitry has been energized, survey for compliance with requirements.

Visually inspect cable insulation for damage. Correct sharp corners, protuberances in cable trays, vibrations, and thermal expansion and contraction conditions, which may cause or have caused damage.

Verify that the number, size, and voltage of cables in cable trays do not exceed that permitted by NFPA 70. Verify that communications or data-processing circuits are separated from power circuits by barriers or are installed in separate cable trays.

Verify that there are no intruding items such as pipes, hangers, or other equipment in the cable tray.

Remove dust deposits, industrial process materials, trash of any description, and any blockage of tray ventilation.

Visually inspect each cable tray joint and each ground connection for mechanical continuity. Check bolted connections between sections for corrosion. Clean and retorque in suspect areas.

Check for improperly sized or installed bonding jumpers.

Check for missing, incorrect, or damaged bolts, bolt heads, or nuts. When found, replace with specified hardware.

Perform visual and mechanical checks for adequacy of cable tray grounding; verify that all takeoff raceways are bonded to cable trays. Test entire cable tray system for continuity. Maximum allowable resistance is 1 ohm.

Prepare test and inspection reports.

PROTECTION

Protect installed cable trays and cables.

Install temporary protection for cables in open trays to safeguard exposed cables against falling objects or debris during construction. Temporary protection for cables and cable tray can be constructed of wood or metal materials and shall remain in place until the risk of damage is over.

Repair damage to galvanized finishes with zinc-rich paint recommended by cable tray manufacturer.

Repair damage to paint finishes with matching touchup coating recommended by cable tray manufacturer.

END OF SECTION 260536